## B
The following performances are based on information received and are to be used for guidance only, When comparing the performance of different drying methods
| Capacity (FAD) |  |  |  | Capacity | 600 | cfm | 283.2 | Litres/ Sec | 1019.52 | M3/Hour
| Pressure (g) |  |  |  |  | 125 | psi (g) | 8.6207 | bar (g)
| Ambient Temperature |  |  |  |  | 83 | °F | 28.3333 | °C
| Load Factor |  | 75 | 75% | Air Usage | 450 | cfm | 212.4 | Litres/ Sec | 764.64 | M3/Hour
| Weekly Hours |  |  | 160
| Weeks Per Annum |  |  | 50 | Annual operating hours |  | 8000
| Relative Humidity |  | 90 | 90%
Water Remaining in Compressed Air
Imperial Units
| Drying Method | Dewpoint | Gallons Week | Gallons Annum
| No Treatment | 165.2 | 658.775 | 32938.7513
| After Cooler | 101 | 129.1084 | 6455.4194
| Deliquescent | 90 | 94.4707 | 4723.5337
| Refrigerant | 37 | 15.5454 | 777.2693
| Desiccant | -40 | 0.33366 | 16.6831
Metric Units
| Drying Method | Dewpoint | Litres Week | Litres Annum
| No Treatment | 74 | 2994.4319 | 149721.5969
| After Cooler | 38.3333 | 586.8563 | 29342.8156
| Deliquescent | 27.3333 | 429.4122 | 21470.6079
| Refrigerant | 3 | 70.6608 | 3533.0424
| Desiccant | -40 | 1.5166 | 75.8325
NOTE MOISTURE VAPOUR WILL NOT SEPARATE INTO WATER DROPLETS UNLESS THE AMBIENT TEMPERATURE IS LESS THAN STATED DEWPOINT TEMPERATURE
658.775
Water In Air Calculator

## Water Content
Dewpoint | Dewpoint | Ammount of | Dewpoint | Dewpoint
°C | °F | gr/m³ | °C | °F
-70 | -94 | 0.0027919 | -70 | -94 | Volume of water contained within incoming air | 2994.4319
-69 | -92.2 | 0.0032212 | -69 | -92.2 | Air temperature before after cooler | 245
-68 | -90.4 | 0.0037119 | -68 | -90.4
-67 | -88.6 | 0.0042715 | -67 | -88.6
-66 | -86.8 | 0.0049084 | -66 | -86.8
-65 | -85 | 0.0056329 | -65 | -85
-64 | -83.2 | 0.0064553 | -64 | -83.2
-63 | -81.4 | 0.0073885 | -63 | -81.4
-62 | -79.6 | 0.0084464 | -62 | -79.6
-61 | -77.8 | 0.0096425 | -61 | -77.8
-60 | -76 | 0.010989 | -60 | -76
-59 | -74.2 | 0.012518 | -59 | -74.2
-58 | -72.4 | 0.014244 | -58 | -72.4
-57 | -70.6 | 0.016175 | -57 | -70.6
-56 | -68.8 | 0.018357 | -56 | -68.8
-55 | -67 | 0.020798 | -55 | -67
-54 | -65.2 | 0.023553 | -54 | -65.2
-53 | -63.4 | 0.026628 | -53 | -63.4
-52 | -61.6 | 0.0030078 | -52 | -61.6
-51 | -59.8 | 0.033935 | -51 | -59.8
-50 | -58 | 0.038244 | -50 | -58
-49 | -56.2 | 0.043046 | -49 | -56.2
-48 | -54.4 | 0.048413 | -48 | -54.4
-47 | -52.6 | 0.054384 | -47 | -52.6
-46 | -50.8 | 0.061038 | -46 | -50.8
-45 | -49 | 0.068423 | -45 | -49
-44 | -47.2 | 0.076632 | -44 | -47.2
-43 | -45.4 | 0.085732 | -43 | -45.4
-42 | -43.6 | 0.095794 | -42 | -43.6
-41 | -41.8 | 0.10696 | -41 | -41.8
-40 | -40 | 0.11934 | -40 | -40
-39 | -38.2 | 0.133 | -39 | -38.2
-38 | -36.4 | 0.14812 | -38 | -36.4
-37 | -34.6 | 0.16475 | -37 | -34.6
-36 | -32.8 | 0.18308 | -36 | -32.8
-35 | -31 | 0.20335 | -35 | -31
-34 | -29.2 | 0.22562 | -34 | -29.2
-33 | -27.4 | 0.25005 | -33 | -27.4
-32 | -25.6 | 0.27689 | -32 | -25.6
-31 | -23.8 | 0.30638 | -31 | -23.8
-30 | -22 | 0.33874 | -30 | -22
-29 | -20.2 | 0.37422 | -29 | -20.2
-28 | -18.4 | 0.41303 | -28 | -18.4
-27 | -16.6 | 0.45549 | -27 | -16.6
-26 | -14.8 | 0.5019 | -26 | -14.8
-25 | -13 | 0.55258 | -25 | -13
-24 | -11.2 | 0.60798 | -24 | -11.2
-23 | -9.4 | 0.66831 | -23 | -9.4
-22 | -7.6 | 0.73412 | -22 | -7.6
-21 | -5.8 | 0.80586 | -21 | -5.8
-20 | -4 | 0.88406 | -20 | -4
-19 | -2.2 | 0.96847 | -19 | -2.2
-18 | -0.4 | 1.0607 | -18 | -0.4
-17 | 1.4 | 1.1607 | -17 | 1.4
-16 | 3.2 | 1.27 | -16 | 3.2
-15 | 5 | 1.3878 | -15 | 5
-14 | 6.8 | 1.5154 | -14 | 6.8
-13 | 8.6 | 1.6538 | -13 | 8.6
-12 | 10.4 | 1.8036 | -12 | 10.4
-11 | 12.2 | 1.9655 | -11 | 12.2
-10 | 14 | 2.1401 | -10 | 14
-9 | 15.8 | 2.329 | -9 | 15.8
-8 | 17.6 | 2.5329 | -8 | 17.6
-7 | 19.4 | 2.7531 | -7 | 19.4
-6 | 21.2 | 2.9912 | -6 | 21.2
-5 | 23 | 3.2469 | -5 | 23
-4 | 24.8 | 3.5225 | -4 | 24.8
-3 | 26.6 | 3.8185 | -3 | 26.6
-2 | 28.4 | 4.1371 | -2 | 28.4
-1 | 30.2 | 4.4804 | -1 | 30.2
0 | 32 | 4.8491 | 0 | 32
1 | 33.8 | 5.1937 | 1 | 33.8
2 | 35.6 | 5.5602 | 2 | 35.6
3 | 37.4 | 5.9483 | 3 | 37.4
4 | 39.2 | 6.3603 | 4 | 39.2
5 | 41 | 6.7974 | 5 | 41
6 | 42.8 | 7.2609 | 6 | 42.8
7 | 44.6 | 7.7482 | 7 | 44.6
8 | 46.4 | 8.2682 | 8 | 46.4
9 | 48.2 | 8.8153 | 9 | 48.2
10 | 50 | 9.3968 | 10 | 50
11 | 51.8 | 10.0124 | 11 | 51.8
12 | 53.6 | 10.6617 | 12 | 53.6
13 | 55.4 | 11.3443 | 13 | 55.4
14 | 57.2 | 12.0675 | 14 | 57.2
15 | 59 | 12.8233 | 15 | 59
16 | 60.8 | 13.6263 | 16 | 60.8
17 | 62.6 | 14.4762 | 17 | 62.6
18 | 64.4 | 15.3649 | 18 | 64.4
19 | 66.2 | 16.2994 | 19 | 66.2
20 | 68 | 17.289 | 20 | 68
21 | 69.8 | 18.3264 | 21 | 69.8
22 | 71.6 | 19.4177 | 22 | 71.6
23 | 73.4 | 20.5646 | 23 | 73.4
24 | 75.2 | 21.7688 | 24 | 75.2
25 | 77 | 23.0339 | 25 | 77
26 | 78.8 | 24.3609 | 26 | 78.8
27 | 80.6 | 25.7542 | 27 | 80.6
28 | 82.4 | 27.2146 | 28 | 82.4
29 | 84.2 | 28.7457 | 29 | 84.2
30 | 86 | 30.3496 | 30 | 86
31 | 87.8 | 32.0299 | 31 | 87.8
32 | 89.6 | 33.7895 | 32 | 89.6
33 | 91.4 | 35.6311 | 33 | 91.4
34 | 93.2 | 37.5574 | 34 | 93.2
35 | 95 | 39.5725 | 35 | 95
36 | 96.8 | 41.6784 | 36 | 96.8
37 | 98.6 | 43.8791 | 37 | 98.6
38 | 100.4 | 46.1785 | 38 | 100.4
39 | 102.2 | 48.5799 | 39 | 102.2
40 | 104 | 51.0857 | 40 | 104
41 | 105.8 | 53.6998 | 41 | 105.8
42 | 107.6 | 56.4328 | 42 | 107.6
43 | 109.4 | 59.272 | 43 | 109.4
44 | 111.2 | 62.2369 | 44 | 111.2
45 | 113 | 65.333 | 45 | 113
46 | 114.8 | 68.5524 | 46 | 114.8
47 | 116.6 | 71.9278 | 47 | 116.6
48 | 118.4 | 75.4172 | 48 | 118.4
49 | 120.2 | 79.0196 | 49 | 120.2
50 | 122 | 82.8009 | 50 | 122
51 | 123.8 | 86.7596 | 51 | 123.8
52 | 125.6 | 90.8272 | 52 | 125.6
53 | 127.4 | 95.0694 | 53 | 127.4
54 | 129.2 | 99.4845 | 54 | 129.2
55 | 131 | 104.0709 | 55 | 131
56 | 132.8 | 108.827 | 56 | 132.8
57 | 134.6 | 113.7513 | 57 | 134.6
58 | 136.4 | 118.8423 | 58 | 136.4
59 | 138.2 | 124.1638 | 59 | 138.2
60 | 140 | 129.6485 | 60 | 140
61 | 141.8 | 135.36 | 61 | 141.8
62 | 143.6 | 141.2961 | 62 | 143.6
63 | 145.4 | 147.3904 | 63 | 145.4
64 | 147.2 | 153.7702 | 64 | 147.2
65 | 149 | 160.3686 | 65 | 149
66 | 150.8 | 167.1839 | 66 | 150.8
67 | 152.6 | 174.214 | 67 | 152.6
68 | 154.4 | 181.5207 | 68 | 154.4
69 | 156.2 | 189.1016 | 69 | 156.2
70 | 158 | 196.8909 | 70 | 158
71 | 159.8 | 205.7232 | 71 | 159.8
72 | 161.6 | 214.4077 | 72 | 161.6
73 | 163.4 | 223.0421 | 73 | 163.4
74 | 165.2 | 231.6267 | 74 | 165.2
75 | 167 | 240.162 | 75 | 167
76 | 168.8 | 250.4113 | 76 | 168.8
77 | 170.6 | 260.602 | 77 | 170.6
78 | 172.4 | 270.7346 | 78 | 172.4
79 | 174.2 | 280.8098 | 79 | 174.2
80 | 176 | 290.8278 | 80 | 176
81 | 177.8 | 302.7843 | 81 | 177.8
82 | 179.6 | 314.6735 | 82 | 179.6
83 | 181.4 | 326.4958 | 83 | 181.4
84 | 183.2 | 338.252 | 84 | 183.2
85 | 185 | 349.9425 | 85 | 185
86 | 186.8 | 363.8248 | 86 | 186.8
87 | 188.6 | 377.63 | 87 | 188.6
88 | 190.4 | 391.3587 | 88 | 190.4
89 | 192.2 | 405.0116 | 89 | 192.2
90 | 194 | 418.5893 | 90 | 194
91 | 195.8 | 434.5922 | 91 | 195.8
92 | 197.6 | 450.5073 | 92 | 197.6
93 | 199.4 | 466.3355 | 93 | 199.4
94 | 201.2 | 482.0775 | 94 | 201.2
95 | 203 | 497.734 | 95 | 203
96 | 204.8 | 516.1707 | 96 | 204.8
97 | 206.6 | 534.5077 | 97 | 206.6
98 | 208.4 | 552.7459 | 98 | 208.4
99 | 210.2 | 570.8861 | 99 | 210.2
100 | 212 | 588.929 | 100 | 212
101 | 213.8 | 609.8529 | 101 | 213.8
102 | 215.6 | 630.6652 | 102 | 215.6
103 | 217.4 | 651.3668 | 103 | 217.4
104 | 219.2 | 671.9587 | 104 | 219.2
105 | 221 | 692.4416 | 105 | 221
106 | 222.8 | 716.3148 | 106 | 222.8
107 | 224.6 | 740.0623 | 107 | 224.6
108 | 226.4 | 763.6852 | 108 | 226.4
109 | 228.2 | 787.1846 | 109 | 228.2
110 | 230 | 810.5612 | 110 | 230
111 | 231.8 | 837.5171 | 111 | 231.8
112 | 233.6 | 864.3329 | 112 | 233.6
113 | 235.4 | 891.01 | 113 | 235.4
114 | 237.2 | 917.5491 | 114 | 237.2
115 | 239 | 943.9516 | 115 | 239
116 | 240.8 | 974.3173 | 116 | 240.8
117 | 242.6 | 1004.5273 | 117 | 242.6
118 | 244.4 | 1034.5828 | 118 | 244.4
119 | 246.2 | 1064.4851 | 119 | 246.2
120 | 248 | 1094.2352 | 120 | 248
121 | 249.8 | 1129.726 | 121 | 249.8
122 | 251.6 | 1165.0372 | 122 | 251.6
123 | 253.4 | 1200.1702 | 123 | 253.4
124 | 255.2 | 1235.126 | 124 | 255.2
125 | 257 | 1269.9061 | 125 | 257
126 | 258.8 | 1304.512 | 126 | 258.8
127 | 260.6 | 1338.9448 | 127 | 260.6
128 | 262.4 | 1375.7065 | 128 | 262.4
129 | 264.2 | 1413.948 | 129 | 264.2
130 | 266 | 1451.9993 | 130 | 266
131 | 267.8 | 1493.5723 | 131 | 267.8
132 | 269.6 | 1534.9401 | 132 | 269.6
133 | 271.4 | 1576.1035 | 133 | 271.4
134 | 273.2 | 1619.2765 | 134 | 273.2
135 | 275 | 1664.9349 | 135 | 275
136 | 276.8 | 1710.37 | 136 | 276.8
137 | 278.6 | 1755.5837 | 137 | 278.6
138 | 280.4 | 1800.5774 | 138 | 280.4
139 | 282.2 | 1845.8402 | 139 | 282.2
140 | 284 | 1895.2594 | 140 | 284